## Slide 1: Development of Rural Electricity Generation Systems using Solar Resources
Quick Utilization of Solar Radiation for Rural Development….
P M V Subbarao
Professor
Mechanical Engineering Department
Head, CRDT

## Slide 2: A Researcher is Blind to Novel Innovation
Must be open to all possible interpretations…..

## Slide 3: Idealized Equivalent circuit of a Solar Cell
Each photon with energy greater than Eg = hg produces one electronic charge q at a voltage of Vg =hg /q.
Net Current in the load
Physical Circuit
Equivalent Functional Circuit

## Slide 4: Capacity of a Solar Cell
The ideal I-V characteristics of a solar cell are given by
The source IL results from the excitation of excess carriers by solar radiation, Is is the diode saturation current, and RL is the load resistance.
The current Density of a P-N Junction cell is

## Slide 5: PV Cell as an Engine-Generator System
Current-voltage characteristics of a solar cell under solar radiation
The curve passes through the fourth quadrant, and therefore power can be extracted from the device.
A load RL is connected to the solar cell as shown in Figure.
The current through the RL is in the opposite direction to the conventional current flow.
The I-V curve is more generally represented by
Notes: I will introduce the principle to begin with.
Solar cell, invented in the USA in 1954, is a kind of semiconductor to convert energy of light directly into electricity. Most semiconductor used for solar cell are silicon semiconductors and it is composed of P-type semiconductor and N-type semiconductor.
Sunlight hitting the cell produces two types of electrons, negatively charged and positively charged electrons in the semiconductors. Negatively charged electrons gather around N-type semiconductor while positively charged electrons gather around P-type semiconductor.
When youconnect loads such as a light bulb or motor, electric current occurs between two electrodes.

## Slide 6: Performance A Real PV Cell with Losses
Notes: I will introduce the principle to begin with.
Solar cell, invented in the USA in 1954, is a kind of semiconductor to convert energy of light directly into electricity. Most semiconductor used for solar cell are silicon semiconductors and it is composed of P-type semiconductor and N-type semiconductor.
Sunlight hitting the cell produces two types of electrons, negatively charged and positively charged electrons in the semiconductors. Negatively charged electrons gather around N-type semiconductor while positively charged electrons gather around P-type semiconductor.
When youconnect loads such as a light bulb or motor, electric current occurs between two electrodes.

## Slide 7
Voltage and Current of PV cell ( I-V Curve )
(V)
(A)
Voltage(V)
Current(I)
Open Circuit
P
N
V
P
N
A
Short Circuit
about 0.5V (Silicon)
Notes: I will introduce the principle to begin with.
Solar cell, invented in the USA in 1954, is a kind of semiconductor to convert energy of light directly into electricity. Most semiconductor used for solar cell are silicon semiconductors and it is composed of P-type semiconductor and N-type semiconductor.
Sunlight hitting the cell produces two types of electrons, negatively charged and positively charged electrons in the semiconductors. Negatively charged electrons gather around N-type semiconductor while positively charged electrons gather around P-type semiconductor.
When youconnect loads such as a light bulb or motor, electric current occurs between two electrodes.

## Slide 8
Isothermal Performance of A Solar cell
I-V Curve
(A)
Voltage(V)
Current(I)
Standard insolation 1.0 kW/m2
0.49 V
0.62 V
4.95A
5.55A
Depend on type of cell or cell-material ( Si = 0.5V )
Depend on cell-size
Max. Power Depend on Solar intensity (insolation)
Notes: I will introduce the principle to begin with.
Solar cell, invented in the USA in 1954, is a kind of semiconductor to convert energy of light directly into electricity. Most semiconductor used for solar cell are silicon semiconductors and it is composed of P-type semiconductor and N-type semiconductor.
Sunlight hitting the cell produces two types of electrons, negatively charged and positively charged electrons in the semiconductors. Negatively charged electrons gather around N-type semiconductor while positively charged electrons gather around P-type semiconductor.
When youconnect loads such as a light bulb or motor, electric current occurs between two electrodes.

## Slide 9
Harvesting of Maximum Power from A Cell
P
N
A
V
To obtain maximum power, current control (or voltage control) is very important.
(V)
(A)
Voltage(V)
Current(I)
I x V = W
P2
PMAX
P1
Vpmax
Ipmax
I/V curve
P- Max control
“Power conditioner” (mentioned later) will adjusts to be most suitable voltage and current automatically.
Power curve

## Slide 10
Operational Point of A Cell
(V)
(A)
Voltage(V)
Current(I)
about 0.5V (Silicon)
Current depend on - Intensity of solar radiation. - Size of cell
Normal operation point (Maximum Power point)
I x V = W
Voltage on normal operation point 0.5V (in case of Silicon PV)
Notes: I will introduce the principle to begin with.
Solar cell, invented in the USA in 1954, is a kind of semiconductor to convert energy of light directly into electricity. Most semiconductor used for solar cell are silicon semiconductors and it is composed of P-type semiconductor and N-type semiconductor.
Sunlight hitting the cell produces two types of electrons, negatively charged and positively charged electrons in the semiconductors. Negatively charged electrons gather around N-type semiconductor while positively charged electrons gather around P-type semiconductor.
When youconnect loads such as a light bulb or motor, electric current occurs between two electrodes.

## Slide 11: Selection of Load for Maximum Power Harvest
Estimate obtained power by I / V curve
(V)
(A)
Voltage(V)
Current(I)
12
10
8
6
4
2
0
0 0.1 0.2 0.3 0.4 0.5 0.6
P
N
A
PV character ( I/V curve )
If the load has 0.05 ohm resistance, cross point of resistance character and PV-Character will be following point.
Then power is 10x0.5=5 W
Resistance character
Ohm’s theory

## Slide 12
Crystalline
Non-crystalline
Single crystal
Poly crystalline
Amorphous
Gallium Arsenide (GaAs)
Conversion Efficiency of Module
10 - 17%
10 - 13%
7 - 10%
18 - 30%
Dye-sensitized Type
Organic Thin Layer Type
7 - 8%
2 - 3%
Silicon Semiconductor
Compound
Semiconductor
Solar
Cell
Organic
Semiconductor
Types and Conversion Efficiency of Solar Cell
Conversion Efficiency =
Electric Energy Output
Energy of Insolation on cell
x
100%
Notes: Variety of solar cell and conversion efficiency
There are 2 major types of solar cell: one using silicon semiconductor and one using compound semiconductor. Solar cell using silicon semiconductor is further divided into crystalline and non-crystalline or amorphous semiconductor.The crystalline type silicon semiconductor is widely used for its high conversion rate and reliability track record. The amorphous type semiconductor performs well even under a fluorescent lamp, so, it is used as a source of power for calculators and wrist watches.
Compound semiconductor’s conversion rate is very high. But it is difficult to obtain.
Organic semiconductor is under development for further reducing cost.

## Slide 13: SOLAR PV MODULE
Solar PV module
A solar PV module is a device in which several solar cells are connected together to generate more power than a single solar cell.
Single solar cell

## Slide 14: Solar Cell to Solar PV Module Why ?
Series connection  Voltage is additive
Single solar cell power = 5.0 Watts
6 cells in series connection  30 Watts

## Slide 15: STAND ALONE PV SYSTEM

## Slide 16
Standalone PV Water Pumping System
Water pumping system

## Slide 17: HYBRID PV SYSTEM

## Slide 18: GRID-TIED PV SYSTEM

## Slide 19: CASE STUDY: “Off-grid Electrification of Village Khaira BegiDistrict -Chatra, Jharkhand, India”.

## Slide 20: Village Khaira Begi District -Chatra, Jharkhand, India”.

## Slide 21: VILLAGE AT A GLANCE
Economy of the village is mainly depended on the agricultural activities.
Paddy is main crop of this village.

## Slide 22: Plant Layout

## Slide 23: PROJECT BRIEF
Installation of a 5.80 kWp stand alone Solar PV Plant
20kWh Panasonic make Lithium Ion battery for energy storage.
Mini Grid has been installed in the villages and each household are through localized distribution line.
During the day time, surplus power will be utilized to run productive load such as rice huller and solar water pumps.
Each house is having a provision of Lighting, Fan and Mobile charging.

## Slide 24: Project Summary

## Slide 25: Tariff Fixation and Revenue Collection
Based on the preliminary interaction, it was found that villagers are willing to pay for the use of power supplied by solar mini grid.
A fixed tariff of 100 Rs. /Months for domestic use
A tariff of 150 Rs./Month for livelihood useslike pump and rice huller.
A village energy committee has been constituted a five members including 2 Male and 3 Female.
To monitor/manage the operational and financial issues.
Village energy committee will also circulate the annual income to all household so that every consumer can know the financial status.

## Slide 26: Present Status

## Slide 27: Measureable Impacts